COÂNG TY TNHH VIEÄT AN TOAØN

27. Baøu Baøng – Phöôøng 13 – Quaän Taân Bình – Tp.Hoà CHí Minh

Tel: 08.8122798 	Email: vietsafe@vnn.vn

TAØI LIEÄU TAÄP HUAÁN

HÖÔÙNG DAÃN LAÉP ÑAËT

TRUNG TAÂM XÖÛ LYÙ CHÖÕA CHAÙY TÖÏ ÑOÄNG FENIX SERIES FC200C (ALARMCOM)

Thaùng 03 naêm 2005

| Presentation. Systems with 2 detection zones Automatic fire-extinguishing systems Scope of application. Input lines for automatic and/or manual detection. Input lines for manual activation. Mixed lines. Pre-alarm output. General siren output line. Automatic alarm output lines for each zone. Transmission outputs. Extinguishing system lines Input lines Output lines System autonomy. Installing the system. Material required Material for the installation Auxiliary material Installation process Installing series FC200C control panels Cabling. Programming the FC210C/220C/220CLC Jumpers Micro-switches Starting up Interpreting the indicators and controls. Zones (lines 1 and 2) General system control section. Fire-extinguishing (FC220C and FC220CLC) Final system test. Simulation of faults Detection lines General siren Fire-extinguishing line (FC220C and FC220CLC) A/C mains failure. Zone disconnection Zone alarm. Fire-extinguishing (FC220C and FC220CLC) Reset and pre-triggering times for the FC220C (Current-limited detectors) Reset and pre-triggering times for the FC220CLC (Non-current-limited detectors) Manual inputs and fire-extinguishing with the FC220C and FC220CLC. ANNEX 1: Calculations for power supply unit and batteries. ANNEX 2: Technical data. ANNEX 3: References for ordering. PRESENTATION. The FC200C series of control panels comprises a range of high-performance micro computer controlled units, able to supervise 2 lines of 24 volt conventional detectors and/or call points and fire-extinguishing output. FC210C controls 2 lines of conventional detectors and/or call points FC220C incorporates an additional control for automatic fire-extinguishing. The panels are fitted with a full range of illuminated indicators, giving system status information, and push buttons for access to the various functions. Additionally, a piezoelectric buzzer gives an acoustic warning of events registered. A telephonic transmitter can be enables so as to report “Fire” and “Fault on line” events to an alarm monitoring centre. The system includes a 27.6V/1.2A power supply and space for two 12V/6.5Ah batteries, which are periodically checked automatically and when certain manual operations are performed via the panel. The correct operation of the power source is signaled by an illuminated indicator. In the event of insufficient battery voltage being detected during any of the aforementioned checks the event is memorized. The internal sounder, which has a number of different sound cadences, signals the occurrence of any of the incidents monitored by the system. If can be inhibited manually, and in the event of a new incident it is automatically reset with the corresponding sound. An illuminates indicator signals this inhibition is effective. Given the relatively large number of illuminated indicators, a push-button switch enables them all to be tested simultaneously. This also tests the internal sounder and runs the manual battery test. There is an option for use of any the controls to require an enable key to be pressed. This makes it possible to minimize the risk of involuntary activations. The FC200C control panels comes installed in a compact kiln dried, epoxy-painted steel case measuring 312mm (width) by 221mm (height) and 71mm (depth). The front panel consists of an attractive, screen-printed plasticized printed plastic panel, which incorporates the text of the indicators and controls on the unit. Systems with 2 detection zones. There are two modes of control panel depending on the type of detector used: FC210C CL: monitors up to 2 lines of current-limited detectors and/or call points. FC210C SL: monitors up to 2 lines of non-current-limited detectors and/or call points. Automatic fire-extinguishing systems. There are two modes of control panel depending on the type of detector used: FC220C: incorporates an additional control for the automatic extinguishing in zone 1. The extinguishing process can be programmed to be triggered upon activation of 2 or 3 current-limited detectors associated with the zone. In this control panel zone 2 can be used to monitor other risk, using conventional detectors of the same type. FC220CLC: incorporates an additional control to perform automatic extinguishing associated with the 2 conventional detection zones fitted non-current-limited detectors based on the crossed-zone criterion. SCOPE OF APPLICATION. Series FC200C control panel are intended for the control of conventional fire detection installations with cover broken up into “zones” comprising 2 or more of the following parts: Up to 2 supervised, automatically or manually activated, conventional detection lines based on twin-core cables. 1 general pre-alarm output. 1 general siren output. Individual automatic output line(s) by zone. Fire and fault outputs for telephone transmission. FC200C and FC200CLC versions equipped with extinguishing functions also incorporate: 1 pre-trigger output line. 1 output line for activation of the extinguishing system electro-valve. 1 output for transmission of extinguishing 2 manual control input lines for the extinguishing system. 1 extinguishing agent pressure control input line. Input lines for automatic and / or manual detection. Series FC200C, controllers manage up to 2 conventional 24V two – core detection lines incorporating a 2K2 Ohms ½ W end of line resistor as a way of supervising the state of the line and identifying possible open-circuit or short-circuit faults.(See Figs 3,5,6 and 7). Input lines for manual activation. These lines are identical to those described above, but instead of automatic detectors, only manual call point press switch causes the contacts of a micro switch to close. (See Figs 4 and 7). Their consumption on activation need to be limited by a resistor fitted inside the device, wired in series with the contacts mentioned above. The press-switches are fitted in parallel along the line. Mixed lines. Similar to those above but with capacity for mixed conventional detectors and call points to be fitted in a similar way to that seen in earlier sections. (See Figs. 5,6,7). Pre-alarm output. Able to switch 1A at 24V through relay free contacts. Instant activation is caused on alarm in any zone, returning to rest once the pre-alarm time elapsed. Not protected by a dedicated fuse. If necessary, use an air fuse. General siren output line. Responsible for the general warning signal. This may or may not be delayed, depending on the pre-alarm time has elapsed. Supplies 24V with a maximum current of 2A, fuse protected, for activation of one or more sirens fitted in parallel on the line. The line is supervised for open- or short-circuit faults by two procedures: When only one siren or bell is used, an end of line module line supervision fitted next to it at the end of the line. (See Fig.8). When several sirens or bells are used, the same module as above for the last siren or bell and a diode of type 1N4005 or 1N4007 for each intermediate siren or bell or simultaneous activation of all of them via a common line. (See Fig.9). Automatic alarm output lines by zone. Enable activation of one or more elements (acoustic or optical), when the line associated with a zone goes into the alarm phase, via a free-contact relay (C, NO, 1A at 24Vdc). See Fig. 11) Transmission outputs. Two open-collector outputs, allows communication of the general fire and fault signals via a remote transmission device. Extinguishing system lines. These are twin-core Input-Output lines for the automatic or manual control of the Extinguishing System. (See Fig. 12). Input lines Manual trigger input (DISP). Immediate extinguishing is enabled via NO (normally open) press switches activated by breaking glass (similar to those used for fire alarms). Manual inhibition input (INH). Similar to the previous input; enables inhibition or halting of the extinguishing system. Manual triggering takes precedence over manual or automatic inhibition (DISABLE/ENABLE push-button on the control panel); i.e. manual extinguishing is always possible in the event of inhibition. Low pressure detection line (P.BAJ.). a NO (normally open) twin-core line which sends the control panel a signal from a pressure start in order to identify a possible drop in the pressure of the extinguishing agent. Output lines. Extinguishing activation lines (EXT). Intended for automatic triggering of the extinguishing system. It provides a voltage of 24 VDC for activation of the electro valve which releases the extinguishing agent. It is supervised for open-or short-circuits faults by means of an end-of-line module installed next to the electro valve (See Fig. 10). Pre-trigger output (PRED) Free contact (C and NO) pre-trigger output of 1A at 24Vdc, for activation of warning devices (sirens and/or luminous signs). Telephone transmission output (TXEXT). Open-collector output, active when extinguishing system is operating. Enables transmission of the event or activation of a relay allowing a warning to be given (Siren, etc.). System autonomy. Autonomy means here the period during which operation can continue in the absence of mains a.c. This autonomy is achieved by a set of batteries associated with the power supply which, under normal conditions, it keeps in a permanent state of charge by it. FC200C series has a power supply capable of delivering 1.2A at 27.6Vdc and space for 2 12V/6.5Ah batteries. The calculation of the battery requirements is given in ANNEX I. INSTALLATION OF THE SYSTEM. One the system has been structured in terms of the distribution of elements and their operation, the elements can be installed. It is necessary to bear in mind that the cable conduits cannot be shard any other service but must be dedicated exclusively to fire detection and protection. The control panel must be sited in a place where there is sufficient space to complete the installation and subsequent maintenance and service operations with ease (Fig. 13). It must also be sited so as to ensure sufficient visibility and ease of operation for the purposes of operating a fire detection installation, i.e. the high-responsibility installation to which it is destined. Material required. Material for the installation. Some or all of the following material may be necessary: FC210, FC220C or FC220CLC control panel. 2 or more 12V, 6.5Ah batteries (See sub-section 2.8 and annex 2). Telephone transmitter. Auxiliary case for installation of transmitter (if applicable). Detectors. Activity indicators. 2k2 ohm ½W end of line resistors. Alarm pushbuttons (call points) Resistors for call points. Control pushbuttons for possible fire extinguishing (trigger or inhibition). Extinguishing system equipment (cylinders of extinguishing agent, electro valve, etc.). 24Vdc fire-alarm sirens and/or bells. Line supervision modules (sirens or electro valve) and 1N4005 or 1N4007 diodes. Illuminated signaling panels. Fire protection systems (fire doors, fire gates in air-conditioning ducts, etc.) and activation elements for them (door retainers, etc) Appropriate cable for each installation (for example: Pirelli, Parasol II flexible 2x1mm²). 3x1mm² cable for power supply at 220V a/c. Rigid or flexible PVC or galvanized steel cable conduit pipe, depending on type of installation. Inspection boxer for joints, changes of direction, etc. Terminals for connections. Small fixings (screws, nuts, clips, flanges, cable markers, labels, etc.). Auxiliary material The type of auxiliary material required depends on the initial state of the installation (whether the pipe infrastructure has been installed) and its type (whether or not there is a false ceiling/floor, etc.). However, in general terms, it includes all the material needed for a normal electrical installation: Trace marker for laying out lines. Hammer action drill. Hammer. Punch. Cable guide. Glycerin or Vaseline to ease the passage of cables. Universal and cutting pliers. Various types of screwdriver. Blow torch for curving conduit pipes. Set of fixed, star and pipe spanners. Tape measure (5m). An appropriate step ladder. Spray or lighter for testing detectors. 60w electrical soldering iron. Solder. Multi-meter. Etc. Installation process. Carry out the installation in the following order: Mark the position of the conduits and devices. The dimensions of the control panel case can be seen in Fig. 13. Cabling infrastructure (installing conduits). Cabling, including a 220Vac mains connection with its corresponding earth connection, taken from a point separate from the general trip switch (it is preferable to install a specific cut out for the detection system). Installation and connection pf the peripheral devices (detector sockets, activity indicators, press-switches, sirens, bells, illuminated indicators, actuators, etc.), centralizing the corresponding ends of the respective lines at the control panel installation point, leaving the tails clearly marked and of adequate length. Fire extinguishing detection lines should be fitted with the appropriate number of detectors for the type of detection selected (double, triple or crossed zones). End of line modules for supervised out-puts (code 801529) can be found, together with the relevant accessories (adhesive separators, etc), in a bag supplied with the unit. They should be fitted inside, or next to, the last element connected to the line to be supervised (Fig. 8 and 10). All intermediate elements must be fitted with the necessary diodes, as specified in Fig. 9. Cable test. Check the resistance using a multi-meter to ensure circuit continuity and correct isolation of the various lines. The detectors will need to be mounted in their sockets before the detection lines can be tested. The resistance of the line will be equal to the value of the line-terminating resistor fitted to the end. Siren lines and electro-valves will give a similar measurement, but it will be necessary to pay particular attention to the polarity of the probes given the diodes fitted in series with the devices or in the line-terminating module. In the case of other types of line it will either be necessary to take into account the type of element fitted at the end or to short circuit the end in order to take the measurement. Also check that the telephone communication system is working properly if a transmitter is used. INSTALLATION OF SERIES FD200C CONTROL PANELS. Take the cover off the units (1 screw) Unscrew the front panel and disconnect the power supply connector. Mark the fixing points on the wall using the case itself. Drill the holds and, after passing the installation cables through the rear slot on the unit, mount the case using the screws and wall fixing plugs supplied. Cabling Follow figures 11, 12 and 14. Connect up the detection lines. Connect the alarm outputs for each zone, if used. Connect the general siren line. If you want to fit an external pre-alarm warning (acoustic or illuminated), use the corresponding output (relay free contacts). If used, connect the extinguishing system components To transmit alarm and fault events by telephone, connect the appropriate out-puts to the channels indicated on the telephone transmitter. Connect the 220Va.c power line and the earth connection to the terminals in the control panel, but do not connect the power (See Fig. 16). PROGRAMMING THE FC210C/220C/220CLC. Jumpers. (See Fig. 15). CN1. Fitted, when the end of line module is used (code 801520) for supervision of the general siren line. Removed if not used. CN2. Fitted: internal fire alarm sounder is silent when the corresponding zone is out of the service. Not fitted: sounds. CN3. Fitted: fire alarm indicator for zone does not light when the corresponding zone is out of service. Not fitted: indicator lights up. CN6. (on the other side of the circuit). Fitted: enables simultaneous use of the general enabling switch in order so the rest of the push-buttons work. Not fitted: not necessary to press enabling button. Micro-switches. Use a small screwdriver to change their state. (See Fig. 15) Type of unit; micro-switch 1 and 2: Without fire extinguishing (FC210C) With fire extinguishing (FC220C and FC220CLC) General pre-alarm time; micro-switches 3 and 4 (FC210C, FC220C and FC220CLC). 0 seconds (instantaneous). 1 minute. 2 minutes. 4 minutes. Pre-trigger time; micro-switches 5 and 6 (FC220C and FC220CLC) 0 seconds (instantaneous). 1 minute. 2 minutes. 4 minutes. Detection line reset time; micro-switches 7 and 8 (FC220C and FC220CLC) 30 seconds (instantaneous). 1 minute. 2 minutes. 4 minutes. Carry out a general check of the wiring. STARTING UP. Insert the detectors in their sockets (if they have been removed) following the tests mentioned in subsection 3.2 Fit the batteries inside the control panel and connect them (See Fig. 16) Wait a few seconds until the system stabilizes. Enable the zones (the corresponding indicators will illuminate) and check that there are no faults, anomalies or alarms. If any anomaly occurs, disconnect the batteries and investigate the cause. If everything is normal, connect the system to mains power (220Va.c). After a few moments the “POWER” (mains) indicator should come on. INTERPRETING THE INDICATORS AND CONTROLS. Zones (Lines 1 and 2) The status of each of the 2 zones is represented by 4 illuminated indicators and connection/disconnection is effected using two push-button switches. The indicators mentioned above signal (Fig. 1) ENABLE/DISABLE: associated with the push-button of the same name. Lights up when the zone is enabled (in service) Goes out when the zone is out of service. This state is indicated by the sounder, which gives a slow intermittent sound. O.C FAULT: Signals an open-circuit fault on the detector line. The line is supervised constantly for the possibility of an open circuit, even if the zone is out of service. S.C FAULT: As the previous case, but in the event of a short-circuit on the detector line. FIRE: Lights up when one or more of the detectors and/or pushbuttons associated with the zone are activated. The fact of a considerable number of detectors going into the “alarm” state does not put the system into the “short-circuit fault” state. Reciprocally, this fault’s arising does not affect the “fire” output or the corresponding indicator. When a zone is disconnected (out of service) the illuminated and acoustic “fire” indicators (buzzer) may, independently and optionally, be activated or not. However, in no case will the alarm be processed by the system (CN2 and CN3 Fig. 15) Includes the following indicators (Fig. 1) General system control section. PRE-ALARM: Indicates, after going into the “fire” state on any of the zones, that the pre-alarm time has begun to be counted down. This time can be set to any of our values between 0 and 4 minutes. This time precedes the activation of the general alarm output. It incorporates a relay out which is activated during the pre-alarm time, thus allowing the state to be signaled by means of an indicator or an external illuminated indicator. ALARM: Signals the activation of the general alarm output. This output can also be activated and deactivated using the alarm output pushbutton “SOUNDES OUTPUT”. SOUNDERS FAULT: Fault on the general alarm output line. GENERAL FAULT: general fault. Lights up in the event of any type of fault. ACKNOWLEDGE: Signals the manual silencing of the acoustic signal (buzzer) caused by one of the various triggering events. POWER: Presence of mains a/c and correct working of the power supply. Goes off during the battery tests described above. BAT: Battery failure. Lights up, memorizing the event, if an inadequate voltage is detected during any of the tests. (See subsection 1). Subsequently goes out if the voltage returns to its correct value. The sounder (buzzer) can operate in any of the following modes: Continuous: A/C mains fault or failure Slow flash: Zone disconnection Rapid flash: alarm The acoustic warning of alarm takes priority over fault and the latter, in turn, over zone disconnection. The control pushbuttons have following functions: SOUNDERS OUTPUT: Enables manual activation of the general siren or bell in cases where this is required, e.g. if it is necessary to evacuate the building. It also enables the siren to be muted, event during the pre-alarm phase. ACKNOWLEDGE: inhibits the internal sounder (buzzer) following its activation as a result of whatever event. A new event will cause it to sound again, with the relevant sound cadence. ENABLE KEY: When accessing a function this button needs to be pressed simultaneously with the relevant button for the function. This mode of operation can be overridden if requires by setting an internal bridge during installation (See bridge CN6 in Fig. 15) TEST LEDS: Lights all the LEDs on the front panel of the unit simultaneously. Also resets the system LEDs after an event has been detected and corrected. The status of the extinguishing module is represented by 5 LEDs. The extinguishing system may be connected or disconnected in automatic mode by pressing the “ENABLE/DISABLE” push-button on the fire extinguishing system panel. Fire-extinguishing (FC220C and FC220CLC) SOUNDERS FAULT: Associated with the push-button of he same name. lit if automatic fire-extinguishing is enabled and off otherwise. To perform these operations press the push-button simultaneously with “ENABLE KEY” push-button if this option has been programmed. (See bridge CN6 in Fig. 15) PREWARNING (PRE-TRIGGER): Lit during the pre-trigger period. RELEASED (Trigger): Indicates activation of the fire-extinguishing electro=valve (When this has been activated by means of a manual trigger push-button. See subsection 2.7 the RELEASED, Trigger, LED will go off if the manual inhibition push-button is pressed, provided it is in the rest state). ALOW PRESS: Indicates a drop in the pressure of the extinguishing agent. O.C/S.C FAULT: Open-circuit or short-circuit fault (respectively) on the fire-extinguishing output line (electro=valve). These will both light up if the manual override push-button is pressed. FINAL SYSTEM TEST. Before describing the test to be carried out it is important to highlight the following point: Any action via the central unit may require the simultaneous pressing of “ENABLE KEY” (push-button enable) and the relevant control. Any event arising will activate the internal sounder (buzzer). This can be inhibited using the “ACKNOWLEDGE” push-button on the general module (the corresponding LED will light up). It will be activated again if another event occurs. Following an incident it is necessary to reset the system after it has been cleared (return to standby). This can be done by pressing the control corresponding to the zone originating the event twice (enable/disable). It may also be necessary to press “TEST LEDS” to clear the illuminated signal. Following this operation it will reactivate if the cause of the event persists or another event arises. Reset the system on completion of each test. The “ACKNOWLEDGE” indicator will go out. Simulation of faults. This lights the corresponding LEDs (as described in the following sections) and activates the internal sounder (buzzer) in continuous mode. Detection lines. Removing the detectors from their sockets will cause an open circuit fault on the detection line. The O.C FAULT LED for the relevant zone and the “GEN. FAULT” LED will light up. Short-circuiting a detection line at any point will cause a short-circuit fault, causing the S.C FAULT LED for the relevant zone and the “GEN. FAULT” LED will light up. General siren. Opening or short-circuiting the general output line at any point will cause the fault “SOUNDERS FAULT” and the “GEN. FAULT” to light up. Remember that jumper CN1 should be removed if no line-termination module is used (See Fig. 15) In this case the general siren line will only be monitored for open-circuit. Fire-extinguishing line (FC220C and FC220CLC). If the electrovalve line is opened at any point the “O.C FAULT” LED on the fire-extinguishing control panel and the “GEN. FAULT” to light up. Short-circuiting the line will cause the S.C FAULT LED on the fire-extinguishing control panel and the “GEN. FAULT” to light up. Remember that jumper CN1 should be removed if no line-termination module is used (See Fig. 12). In this case the extinction line will only be monitored for open-circuit. A/C mains failure. If mains power is lost the relevant indicator will go out and the internal sounder will signal the event with a continuous tone. The buzzer can be silenced using the “ACKNOWLEDGE” push-button. Zone disconnection. This causes the “ENABLE/DISABLE” indicator to go out and activates the internal sounder in slow intermittent mode. The same thing happens in the case of system override in automatic mode. Zone alarm. A spray should be used to activate the fire detectors in each of the zones one by one. The operation of the manual call-points should be checked using an accessory which allows them to be tested without breaking the glass. When triggered, a detector or call point will cause the “FIRE” indicator corresponding to the zone to light up and the buzzer will emit a rapid intermittent signal. The automatic zone output will be activated. At the same time the “PRE-ALARM” LED will light up on the general control panel. The pre-programmed pre-alarm time will begin to count (this can be zero) and the pre-alarm output will be activated (See subsection 5.2) If the zone is not disconnected, or the “SOUNDERS OUTPUT” is pressed before the pre-alarm time has elapsed, the “ALARM” LED will be lit on the general control panel and the sirens on the general alarm output will be activated. At the same time the “PRE-ALARM” LED will go out and the associated output will be deactivated. After the general alarm output has been activated it can be muted using the “SOUNDERS OUTPUT” push-button on the general control panel. CAUTION: this test can be performed with the zone out of service if jumper CN2 is removed (See Fig. 15). This makes it possible to test the activation of the zone without the risk of triggering the siren. Fire extinguishing (FC220C and FC220CLC). CAUTION: ENSURE THAT THE ELECTRO-VALVE IS DISCONNECTED FROM THE BOTTLE BEFORE PERFORMING THIS TEST. Reset and Pre-triggering times for the FC220C (Current-limited detectors). Zone 1 will used for fire-extinguishing. When the first detector is activated the “reset time” begins to be counted, such that if it elapses without a second detector going into the alarm state (See Fig. 15) the line of detectors associated with zone 1 will automatically be reset for approximately 4 seconds. The original alarm will disappear if the detector(s) is/are not re-triggered. If a second detector goes into the alarm state before this period has elapsed either of two things can happen: Start of possible “pre-trigger time” (double detection). PREWARNING LED will light up. Start of a second “reset time” (triple detection). In the latter case it repeats as described earlier, such that if a third (or more) detector is triggered before the end of the reset time the possible “pre-trigger time” will start and the corresponding output will be activated (See subsection 2.8.2) Reset and Pre-triggering times for the FC220CLC (Non-Current-limited detectors). Two zone are needed for fire-extinguishing. If an alarm is cause in one of the two zones the “reset time” will start; if no alarm has arisen in any other zone at the end of the period the control panel will automatically reset the two detector lines associated with the two zones for approximately 4 seconds. This may cause the original alarm to disappear if the detector does not reactivate, otherwise it will start counting the reset time again and so repeat the process. If after one of the zone has gone into the alarm state an alarm occurs in another zone before the end of the reset time, the possible “pre-trigger time” will begin, and the corresponding output will be activated (See subsection 2.8.2) Manual inputs and fire-extinguishing with the FC220C and FC220CLC. If the “pre-trigger time” (PREWARNING LED will light up) ends without user action the extinguishing system electro-valve will trigger (without discharge of gas in this case) and the “RELEASED” (Trigger) LED will light up. Triggering can be avoided during this period by pressing the remote stop push-button (manual inhibition), or by using the “ENABLE/DISABLE” push-button on the panel. It is also possible to trigger the fire-extinguishing system manually at any time using the remote “manual trigger” push-button (See subsection 2.8.1 and 7.3) | Giôùi thieäu Heä thoáng coù 2 zones doø tìm. Heä thoáng coù chöùc naêng chöõa chaùy töï ñoäng Phaïm vò öùng duïng Line tín hieäu ñi vaøo töï ñoäng vaø, hoaëc tröïc tieáp. Kích hoaït tröïc tieáp Thích öùng ña tín hieäu. Trì hoaõn chôø xaùc nhaän cuûa tín hieäu baùo chaùy thöù 2 Xuaát ra nhieàu ña tín hieäu baùo ñoäng Töï ñoäng kích öùng tín hieäu ra vôùi töøng zone. Xuaát ra tín hieäu chöõa chaùy. Tín hieäu cuûa heä thoáng bao goàm: Tín hieäu ñaàu vaøo Tín hieäu ñaàu ra Coù khaû naêng hoaït ñoäng ñoäc laäp. Laép ñaët heä thoáng. Vaät tö caàn thieát Vaät tö chính Vaät tö phuï Quy trình laép ñaët Laép ñaët Trung taâm xöû lyù series FC200C Coâng taùc laép ñaët daây tín hieäu Laäp trình Trung taâm FC210C/220C/220CLC Caùc coâng taéc daïng caàu noái (Jumpers) Caùc coâng taéc vi maïch Khôûi ñoäng heä thoáng Chuyeån hoùa vaø kieåm soaùt tín hieäu Tín hieäu giaùm saùt (lines 1 and 2) Caáu hình cuûa heä thoáng. Tín hieäu chöõa chaùy (FC220C and FC220CLC) Test heä thoáng. Giaû ñònh tình traïng loãi kyõ thuaät treân: Tín hieäu giaùm saùt Tín hieäu baùo ñoäng Tín hieäu chöõa chaùy (FC220C vaø FC220CLC) Maát nguoàn AC. Zone khoâng ñaáu noái Tín hieäu baùo ñoäng Tín hieäu chöõa chaùy (FC220C vaø FC220CLC) Reset vaø trì hoaõn cho Trung taâm FC220C (Coù giôùi haïn doøng cuûa tín hieäu giaùm saùt) Reset vaø trì hoaõn cho Trung taâm FC220CLC (Khoâng giôùi haïn doøng cuûa tín hieäu giaùm saùt) Khôûi ñoäng tröïc tieáp vaø chöõa chaùy baèng Trung taâm FC220C vaø FC220CLC ANNEX 1: Tính toaùn nguoàn cuûa heä thoáng ANNEX 2: Thoâng soá kyõ thuaät. ANNEX 3: Tham khaûo. GIÔÙI THIEÄU Caùc trung taâm xöû lyù thuoäc series FC200C laø taäp hôïp caùc caáu hình vi xöû lyù kyõ thuaät cao, coù khaû naêng giaùm saùt 2 lines (thieát bò doø khoùi, nhieät… hoaëc coâng taéc baùo ñoäng khaån duøng cho heä thoáng baùo chaùy thuaàn hoaëc heä thoáng chöõa chaùy töï ñoäng) - ñieän aùp 24 volt FC210C giaùm saùt 2 lines doø tìm phaân vuøng FC220C ñöôïc keát hôïp theâm boä xöû lyù chöõa chaùy töï ñoäng Trung taâm xöû lyù bao goàm ñaày ñuû caùc tín hieäu thoâng baùo baèng ñeøn veà tình traïng cuûa heä thoáng, caùc nuùt nhaán truy caäp, laäp trình caùc chöùc naêng khaùc nhau cuûa heä thoáng. Ngoaøi ra, coøn coù coøi nhoû (buzzer) caûnh baùo caùc söï coá kyõ thuaät hieän haønh. Coù 01 ngoõ tín hieäu ñieän thoaïi töông thích cho vieäc ñaáu noái heä thoáng vôùi PCCC sôû taïi (114) ñeå thoâng baùo tín hieäu hoûa hoaïn, loãi kyõ thuaät Trung taâm hoaït ñoäng baèng nguoàn 27.6V/1.2A vaø coù 2 bình ñieän döï phoøng 12V/6.5Ah, Trung taâm coù chöùc naêng töï kieåm tra tình traïng ñònh kyø vaø kieåm tra nhaân coâng tröïc tieáp taïi tuû trung taâm. Khi ñöôïc caáp nguoàn ñaït yeâu caàu, Trung taâm hieån thò ñeøn baùo. Caùc söï kieän maát nguoàn ñieän chính hoaëc nguoàn döï phoøng khoâng ñaït yeâu caàu cuõng ñöôïc ghi nhaän vaøo boä nhôù vaøo baát kyø thôøi ñieåm naøo. Coøi nhoû beân trong Tuû trung taâm coù caùc taàn soá vaø aâm thanh ña daïng ñeå thoâng baùo töông öùng vôùi nhöõng söï coá hoaëc tình traïng cuûa Trung taâm. Neáu coù tín hieäu baùo giaû, heä thoáng seõ töï kieåm tra vaø töï ñoäng khoâi phuïc laïi tình traïng ban ñaàu (reset). Trung taâm coù nuùt nhaán kieåm tra tình traïng caùc ñeøn baùo trong cuøng moät luùc. Vieäc kieåm tra baèng nuùt naøy cuõng cho pheùp kieåm tra tín hieäu coøi nhoû vaø nguoàn döï phoøng. There is an option for use of any the controls to require an enable key to be pressed. This makes it possible to minimize the risk of involuntary activations. Trung taâm ñöôïc baûo veä baèng voû hoäp choáng nhieät, sôn tónh ñieän roäng 312mm, cao 221mm vaø daøy 71mm. Maët tröôùc coù giao dieän gaàn guõi, deã söû duïng baèng moät baûng plastic in saün ñaày ñuû caùc thoâng tin baèng chöõ yù nghóa caùc ñeøn vaø chöùc naêng cuûa heä thoáng Loaïi Trung taâm coù 2 vuøng giaùm saùt Coù 2 loaïi: FC210C CL: giaùm saùt ñeán 2 lines coù giôùi haïn trò soá doøng cuûa line thieát bò doø tìm vaø coâng taéc baùo ñoäng khaån. FC210C SL: giaùm saùt ñeán 2 lines khoâng giôùi haïn trò soá doøng cuûa line thieát bò doø tìm vaø coâng taéc baùo ñoäng khaån. Loaïi duøng cho chöõa chaùy töï ñoäng. Coù 2 loaïi: FC220C: keát hôïp theâm boä xöû lyù chöõa chaùy töï ñoäng cho vuøng 1. Coù theå phaân tích, xöû lyù ñoàng thôøi tín hieäu cuûa 2 hoaëc 3 thieát bò giaùm saùt cuûa cuøng 1 line. Zone 2 ñöôïc duøng vaøo khu vöïc caàn giaùm saùt khaùc FC220CLC: ñöôïc keát hôïp vôùi boä xöû lyù chöõa chaùy töï ñoäng coù chöùc naêng kieåm tra cheùo tín hieäu baùo chaùy cuûa 2 line trong cuøng 1 zone theo tieâu chuaån veà chöõa chaùy töï ñoäng (haïn cheá tình traïng baùo giaû). PHAÏM VI ÖÙNG DUÏNG. Trung taâm xöû lyù Series FC200C laø daïng Trung taâm xöû lyù baùo chaùy daïng quy öôùc. Noù bao goàm toái thieåu 2 trong caùc chöùc naêng sau 2 zone giaùm saùt, töï ñoäng hoaëc kích hoaït baèng tay, line giaùm saùt daïng quy öôùc vôùi caùp tín hieäu 2 daây. 1 ngoõ tín hieäu alarm toång. 1 ngoõ tín hieäu baùo ñoäng. Tín hieäu ngoõ ra cho töøng zone hoaëc nhieàu Cho pheùp xuaát tín hieäu baùo ñoäng vaø tín hieäu baùo loãi ra thieát bò coång telephone Caáu hình FC200C and FC200CLC vôùi chöùc naêng chöõa chaùy töï ñoäng coøn coù theâm caùc ñaëc tính sau: 1 ngoõ ra tín hieäu kích hoaït khôûi ñoäng toå hôïp chöõa chaùy (toå hôïp bình CO2. 1 ngoõ ra tín hieäu khôûi ñoäng caùc van ñieän töø choïn khu vöïc chöõa chaùy. 1 ngoõ ra ñeán boä phaùt tín hieäu cuûa toå hôïp chöõa chaùy. 2 ngoõ tín hieäu vaøo khôûi ñoäng baèng tay cho toå hôïp chöõa chaùy 1 ngoõ tín hieäu vaøo cho boä doø aùp löïc (duøng ñeå baùo caùo tình traïng cuûa toå hôïp chöõa chaùy cho Trung taâm xöû lyù) Tín hieäu vaøo cuûa line giaùm saùt (töï ñoäng vaø/hoaëc khôûi ñoäng baèng tay) Series FC200C, quaûn lyù ñeán 2 zone giaùm saùt daïng quy öôùc ñieän aùp 24V (2 daây) vôùi ñieän trôû cuoái tuyeán 2K2 Ohms ½ W. FC200C cho pheùp töï giaùm saùt tình traïng cuûa tuyeán caùp vaø nhaän daïng caùc loãi kyõ thuaät – ngaén doøng hoaëc maïch hôû. Tín hieäu vaøo cuûa khôûi ñoäng tröïc tieáp baèng tay. Caùc ngoõ tín hieäu vaøo naøy cuõng gioáng nhö caùc ngoõ tín hieäu ñaàu vaøo ñaõ moâ taû ôû treân, nhöng thay cho caùc thieát bò doø tìm töï ñoäng laø chæ goàm caùc coâng taéc khôûi ñoäng khaån baèng tay (Figs 4 vaø 7). Caùc coâng taéc naøy cho pheùp ñaáu song song treân khoaûng caùch khaù daøi Tín hieäu vaøo daïng hoãn hôïp. Töông töï 2 daïng treân nhöng soá löôïng... (Figs. 5,6,7). Tín hieäu trì hoaõn cuûa kích hoaït Caàn coù moät coâng taéc 1A - 24V ñeå caét cheá ñoä trì hoaõn cuûa kích hoaït, döøng ñoàng hoà ñeám thôøi gian cuûa quaù trình naøy Khoâng söû duïng caàu chì baûo veä cho ngoõ tín hieäu naøy. Neáu caàn thieát cho pheùp söû duïng loaïi caàu chí baèng khí. Tín hieäu baùo ñoäng baèng coøi caûnh baùo. Coù chöùc naêng phaùt ñi tín hieäu caûnh baùo toång hôïp. Tín hieäu naøy coù theå ñöôïc trì hoaõn hoaëc khoâng trì hoaõn, ñöôïc duøng ñeå thoâng baùo quaù trình trì hoaõn kích hoaït ñaõ hoaït ñoäng. Ngoõ tín hieäu naøy ñöôïc cung caáp nguoàn 24V vaø doøng max leân ñeán 2A, coù caàu chì baûo veä, coù theå laép ñaët theâm moät coøi nhoû (hoaëc nhieàu hôn) baèng caùch ñaáu song song töø coång ra cuûa tuyeán naøy Tuyeán naøy ñöôïc giaùm saùt tình traïng ngaén doøng hoaëc maïch hôû baèng baèng caùch ñaáu noái theo 2 phöông aùn: Khi chæ söû duïng 1 coøi (nhoû) hoaëc chuoâng vaø 1 thieát bò khaùc, coøi phaûi ñöôïc ñaët ôû cuoái tuyeán. (Fig.8). Khi söû duïng nhieàu coøi hoaëc chuoâng, caùc coøi vaø chuoâng naøy phaûi ñöôïc ñaáu nhö thieát bò noùi treân vôùi 1 diode loaïi 1N4005 hoaëc 1N4007 cho moãi coøi vaø chuoâng ñoù. (Fig.9). Caùc ngoõ tín hieäu ra cuûa zone Cho pheùp kích hoaït moät hoaëc nhieàu yeáu toá (nghe ñöôïc hoaëc thaáy ñöôïc). Khi ngoõ tín hieäu naøy coù lieân keát vôùi zone ñaõ ñöôïc khích hoaït, noù seõ taùc ñoäng ñeán 1 coâng taéc relay (C, NO, 1A - 24Vdc). (Fig. 11) Ngoõ tín hieäu phaùt taùn. Coù 2 coång caâng taéc thöôøng môû cho pheùp göûi tín hieäu thoâng tin baùo chaùy hoaëc baùo loãi kyõ thuaät cho thieát bò giaùm saùt khaùc (Thí duï: CS.PCCC …) Ngoõ tín hieäu ñeán toå hôïp chöõa chaùy töï ñoäng Coù 2 tuyeán (ra vaø vaøo) cho toå hôïp chöõa chaùy töï ñoäng hoaëc baùn töï ñoäng. (See Fig. 12). Tín hieäu ngoõ vaøo Ngoõ tín hieäu khôûi ñoäng baèng tay (DISP). Nhaán coâng taéc khôûi ñoäng khaån (hoaëc ñaäp kính) ñeå vaän haønh laäp töùc toå hôïp chöõa chaùy thoâng qua coâng taéc thöôøng môû (NO – normally open) – töông töï nhö coâng taéc khaån duøng cho baùo chaùy Manual inhibition input (INH). Gioáng nhö loaïi treân. Coù theå haïn cheá (kieåm tra ñoä xaùc thöïc) hoaëc ñöôïc trì hoaõn (thôøi gian chôø kích hoaït) tín hieäu göûi ñeán toå hôïp chöõa chaùy. Khôûi ñoäng tröïc tieáp baèng tay vaøo toå hôïp chöõa chaùy: khôûi ñoäng tröïc tieáp vaøo toå hôïp chöõa chaùy baèng nuùt nhaán treân Tuû trung taâm – coù nghóa laø coù theå can thieäp quaù trình khôûi ñoäng toå hôïp chöõa chaùy baèng tay. Low pressure detection line (P.BAJ.). 1 coâng taéc thöôøng môû NO (normally open) vôùi 2 ñoâi daây seõ göûi tín hieäu töø coâng taéc aùp löïc (thaáp) doø aùp löïc cuûa toå hôïp chöõa chaùy. Tín hieäu ngoõ ra Caùc ngoõ tín hieäu khôûi ñoäng toå hôïp chöõa chaùy (EXT). Ñöôïc ñònh saün cho chöùc naêng chöõa chaùy töï ñoäng cuûa heä thoáng. Ñöôïc cung caáp moät ñieän aùp 24 VDC ñeå ñieàu khieån van choïn khu vöïc phun chaát chöõa chaùy. Ngoõ tín hieäu naøy ñöôïc giaùm saùt tình traïng ngaén doøng hoaëc loãi kyõ thuaät baèng caùch laép ñaët moät ñieän trôû cuoái tuyeán phía sau van choïn khu vöïc phun (Fig. 10). Cheá ñoä trì hoaõn tín hieäu khôûi ñoäng toå hôïp chöõa chaùy (PRED) coù moät coâng taéc (NC vaø NO) ñeå laép moät thieát bò caûnh baùo (coøi, chuoâng) cho quaù trình trì hoaõn tín hieäu khôûi ñoäng toå hôïp chöõa chaùy. Ngoõ tín hieäu phaùt taùn cho ñöôøng truyeàn ñieän thoaïi (TXEXT). Toång hôïp caùc tín hieäu ngoõ ra. Ñöôïc khôûi ñoäng khi toå hôïp chöõa chaùy ñöôïc vaän haønh. Ngoõ tín hieäu naøy cho pheùp phaùt taùn thoâng baùo caùc söï kieän, quaù trình kích hoaït caùc relay ñeán nôi nhaän (coøi, chuoâng, traïm PCCC…) System autonomy. Coù theå hoaït ñoäng maø khoâng caàn nguoàn A.C Nguoàn döï phoøng ñöôïc naïp oån ñònh trong thôøi gian coù ñieän löôùi. Khi maát ñieän löôùi heä thoáng seõ töï ñoäng chuyeån sang söû duïng nguoàn döï phoøng 24VDC Series FC200C cung caáp moät nguoàn ñieän 1.2A - 27.6Vdc (2 boä aéc-quy12V/6.5Ah) ñeå duy trì nguoàn döï phoøng naøy. Coâng thöùc tính toaùn nguoàn döï phoøng xem taïi Phuï luïc I (ANNEX I). LAÉP ÑAËT HEÄ THOÁNG. Ñaây laø moät heä thoáng chæ coù theå hoaït ñoäng ñöôïc khi taát caû caùc phaàn töû caáu thaønh ñöôïc laép ñaët vaø vaän haønh toát. Caùp tín hieäu phaûi ñöôïc baûo veä trong oáng vaø khoâng duøng chung cho baát kyø muïc ñích naøo khaùc. Tuû trung taâm xöû lyù phaûi ñöôïc ñaët taïi nôi coù ñaày ñuû khoâng gian cho coâng taùc laép ñaët vaø baûo haønh sau naøy cuõng nhö söû duïng thuaän lôïi (Fig. 13). Tuû trung taâm xöû lyù caàn phaûi laép ñaët ôû vò trí sao cho taàm nhìn khoâng bò che khuaát vaø thuaän lôïi cho vieäc laép ñaët caùc thieát bò, vaät tö khaùc. Caàn coù söï truø bò, thieát keá saün saøng cho vieäc laép ñaët heä thoáng. Caùc vaät tö caàn thieát. Vaät tö cho coâng taùc laép ñaët. Tuû trung taâm xöû lyù FC210, FC220C hoaëc FC220CLC 2 (hoaëc nhieàu hôn) bình ñieän khoâ12V, 6.5Ah (Xem phaàn 2.8 and Phuï luïc 2). Ñöôøng daây truyeàn taûi tín hieäu ñieän thoaïi. Phuï kieän cho vieäc laép ñaët boä phaùt taùn tín hieäu thoâng qua ñöôøng truyeàn ñieän thoaïi (neáu coù yeâu caàu) Ñaàu doø caùc loaïi (khoùi, nhieät, gas) Caùc ñeøn baùo (neáu coù yeâu caàu) Ñieän trôû cuoái tuyeán 2k2 ohm - ½W Nuùt nhaán baùo ñoäng khaån caáp Ñieän trôû duøng cho coâng taéc khaån coù keøm telephone Caùc nuùt nhaán duøng cho chöùc naêng chöõa chaùy (Nuùt nhaán khôûi ñoäng khaån caáp hoaëc nuùt nhaán keùo daøi thôøi gian trì hoaõn, nuùt nhaán reset heä thoáng) Thieát bò cuûa toå hôïp chöõa chaùy (Bình chöùa chaát chöõa chaùy, van ñieän töø choïn khu vöïc chöõa chaùy…). 24Vdc Coøi hoaëc chuoâng baùo chaùy Caùc tuyeán daây tín hieäu duøng vaøo muïc ñích giaùm saùt tình traïng cuûa caùc thieát bò quan troïng khaùc (coøi, van ñieän töø choïn khu vöïc phun) vaø naén doøng1N4005 or 1N4007 (diode). Baûng höôùng daãn söû duïng, chæ baùo yù nghóa caùc tín hieäu thoâng baùo. Caùc heä thoáng baûo veä, choáng chaùy (cöûa ngaên chaùy, cöûa töï ñoäng cuûa caùc ñöôøng oáng thoâng gioù…) vaø caùc vaät tö phuï cuûa caùc thaønh phaàn naøy. Caùp tín hieäu thích hôïp (thí duï: Pirelli, Parasol II flexible 2x1mm²). Caùp nguoàn 3x1mm² - 220V a/c. OÁng PVC cöùng hoaëc meàm, oáng theùp deõo traùng keõm ñeå luoàn caùp thích öùng vôùi moâi tröôøng laép ñaët. Caùc hoäp kieåm tra taïi caùc ñieåm noái, reõ caùp Thieát bò ñaàu cuoái. Vaät tö phuï (ñinh vít, buloâng, moùc keïp oáng, noái oáng,… Vaät tö phuï Phuï thuoäc vaøo yeâu caàu laép ñaët cuûa töøng coâng trình. Tuy nhieân moät soá vaät tö phuï cuûa coäng taùc laép ñaët thieát bò ñieän sau cuõng caàn thieát cho coâng taùc naøy: Duïng cuï ñaùnh daáu daây, ño ñaïc… Khoan chuyeân duøng (coù va ñaäp) Buùa Keàm nhoå ñinh. Daây keùo caùp Daàu nhôøn giaûm ma saùt cho coâng vieäc keùo raõi caùp Keàm ña duïng vaø keàm caét Caùc loaïi ñinh vít Ñieän trôû uoán oáng PVC hoaëc duïng cuï uoán oáng Duïng cuï coá ñònh oáng (eâtoâ keïp oáng) Thöôùc daây (5m). Thang chöõ A hoaëc tuøy choïn Bình xòt hoaù chaát test ñaàu doø khoùi, nguoàn nhieät test ñaàu doø nhieät Maùy haøn daây 60w Maùy haøn saét Ñoàng hoà ña naêng (V.O.M). Quy trình laép ñaët. Carry out the installation in the following order: Ñaùnh daáu caùc vò trí laép ñaët oáng vaø thieát bò. Kích thöôùc Tuû trung taâm xöû lyù coù theå xem taïi hình 13 (Fig. 13). Keùo raõi caùp tín hieäu cho caùc thieát bò (laép ñaët oáng luoàn). Coâng taùc ñi daây, bao goàm keùo raõi nguoàn 220Vac (coù noái ñaát an toaøn) phaûi ñöôïc caùch ly (neáu coù theå, neân caùch ly khoûi tuyeán caùp tín hieäu giaùm saùt). Laép ñaët vaø ñaáu noái caùc thieát bò ngoaïi vi (ñaàu doø caùc loaïi, ñeøn baùo tình traïng, nuùt nhaán, coâng taéc khaån, coøi, chuoâng …). Laép ñaët vaø Kieåm tra tính hôïp lyù caùc ñieåm ñaáu noái taïi Tuû trung taâm cuûa caùc tuyeán caùp. Laép ñaët caùc tuyeán tín hieäu cuûa heä thoáng chöõa chaùy sao cho töông öùng, thích hôïp vôùi soá löôïng thieát bò ñöôïc laép vaø soá löôïng caùp tín hieäu treân moãi tuyeán cuõng phaûi ñaày ñuû ñoái vôùi töøng loaïi thieát bò doø tìm seõ ñöôïc laép ñaët (2,3 hoaëc 4 daây) Thieát bò giaùm saùt tình traïng cuûa tuyeán tín hieäu ngoõ ra vaø caùc löïa choïn khaùc theâm vaøo (relay,…) : coøi, chuoâng caûnh baùo, ñeøn nhaùy… (code 801529). Taát caû nhöõng thaønh phaàn treân ñöôïc laép ñaët beân trong Tuû hoaëc noái tieáp treân tuyeán caùp caàn ñöôïc giaùm saùt (Fig. 8 and 10). Taát caû phaûi ñöôïc baûo veä baèng naén doøng nhö lyù thuyeát taïi Fig. 9. Test caùp tín hieäu. Kieåm tra taát caû caùc ñieän trôû ñöôïc duøng baèng ñoàng hoà ño ñieän trôû vaø chaéc chaén ñaõ doøng ñöôïc lieân tuïc treân suoát tuyeán tín hieäu, ñoàng thôøi ñaõ ñöôïc coâ laäp rieâng bieät. Caùc ñaàu doø phaûi ñöôïc laép ñaët vaøo caùc ñeá cuûa ñaàu doø tröôùc khi test Ñieän trôû ño ñöôïc cuûa tuyeán tín hieäu phaûi töông öùng vôùi ñieän trôû cuoái tuyeán cuûa tuyeán tín hieäu ñoù. Coøi vaø van ñieän töø phaûi coù thoâng soá töông ñöông, Caàn quan taâm ñeán tính phaân cöïc cuûa ñieän aùp ñaët leân caùc naén doøng (diode) ñöôïc laép cuøng vôùi thieát bò hoaëc caùc duïng cuï ño treân tuyeán. Trong tröôøng hôïp khaùc baét buoäc phaûi ñöa vaøo caùc thieát bò ño ñeám, tính toaùn khaùc taïi cuoái tuyeán hoaëc ñeå ngaén doøng taïi cuoái tuyeán caàn ñöôïc ño ñaïc, tính toaùn vaø kieåm tra caån thaän Cuõng caàn kieåm tra ñöôøng truyeàn ñieän thoaïi moät caùch caån thaän neáu coù söû duïng thieát bò phaùt taùn tín hieäu qua ñöôøng truyeàn naøy. INSTALLATION OF SERIES FD200C CONTROL PANELS. Take the cover off the units (1 screw) Khoâng söû duïng ñinh vít leân maët tröôøc cuûa Tuû trung taâm vaø caùch ly nguoàn ñieän Duøng voû tuû ñaùnh daáu caùc loå khoan cho vít coá ñònh Tuû treân töôøng. Khoan loå, sau ñoù luoàn caùp tín hieäu qua loå coù saún cuûa voû tuû. Coá ñònh voû tuû baèng ñinh vít vaøo töôøng vaø caém caùc phích caém caàn thieát. Coâng taùc laép ñaët caùp tín hieäu vaøo tuû Trung taâm Hình 11, 12 vaø 14. Ñaáu noái caùp vaøo Tuû trung taâm Ñaáu noái ngoõ tín hieäu ra cuûa töøng zone (neáu coù söû duïng) Ñaàu noái coøi caûnh baùo Neáu muoán laép ñaët caùc löïa choïn môû roäng töø ngoõ tín hieäu cuûa cheá ñoä trì hoaõn chôø kích hoaït (hieån thò baèng tín hieäu nghe hoaëc thaáy ñöôïc) thì phaûi choïn loaïi coù thoâng soá thích hôïp (coâng taéc relay töï do) Sau ñoù ñaáu noái vôùi toå hôïp chöõa chaùy töï ñoäng. Ñeå chuyeån tín hieäu baùo ñoäng hoaëc baùo loãi kyõ thuaät baèng ñöôøng truyeàn telephone, ñaáu noái tín hieäu ngoõ ra ñeán boä phaùt taùn tín hieäu Laép ñaët caùp nguoàn 220Va.c cho tuû vaø noái ñaát cho Tuû trung taâm nhöng chöa neân ñaáu nguoàn vaøo tuû trung taâm (Fig. 16). PROGRAMMING THE FC210C/220C/220CLC. Caùc coâng taéc daïng caàu noái. (Fig. 15). CN1. Phuø hôïp :khi phaàn cuoái cuûa daûy module ñöôïc söû duïng (maê 801520 ) ñeå giaùm saùt heä thoáng toång cuûa coøi baùo Gôû boû neáu khoâng söû duïng CN2. Phuø hôïp : coøi baùo chaùy beân trong khoâng baùo khi vuøng töông öùng khoâng coù hoïat ñoäng Khoâng phuø hôïp : aâm thanh CN3. Phuø hôïp : Ñeøn baùo chaùy khoâng saùng leân khi vuøng töông öùng khoâng coù hoïat ñoäng Khoâng phuø hôïp :ñeøn baùo chaùy saùng CN6. (phaàn khaùc cuûa ñöôøng daây). Phuø hôïp : cho pheùp duøng cuøng luùc vôùi coâng taéc toång ñeå cho caùc nuùt aán ngöng laøm vieäc Khoâng phuø hôïp : khoâng caàn thieát aán nut Enabling Coâng taéc chính xaùc : Duøng 1 tuoác nô-vít nhoû ñeå chuyeån traïng thaùiû ( Fig. 15) Kieåu daùng :coâng taéc 1 & 2 Khoâng coù heä thoáng chöõa chaùy (FC210C) Coù heä thoáng chöõa chaùy (FC220C and FC220CLC) Toång quaùt veà thôøi gian cuûa chuoâng baùo : micro-switches 3 vaø 4 (FC210C, FC220C vaø FC220CLC). 0 giaây (ngay töùc thì). 1 phuùt 2 phuùt 4 phuùt Pre-trigger time; micro-switches 5 and 6 (FC220C and FC220CLC) 0 giaây (ngay töùc thì). 1 phuùt 2 phuùt 4 phuùt Ñöôøng doø aán dònh thôøi gian ; micro-switches 7 and 8 (FC220C and FC220CLC) 30 giaây (ngay töùc thì). 1 phuùt 2 phuùt 4 phuùt Kieåm tra toång quaùt ñöôøng daây KHÔÛI ÑOÄNG : Caém ñaàu doø kieåm travaøo oå caém (neáu noù ñaõ bò thaùo ra) theo höôùng daån thöû nghieäm ôû phaàn phuï 3.2 Laép pin vaøo baûng ñieàu khieån (Xem Fig. 16) Chôø vaøi giaây cho ñeán khi heä thoáng oån ñònh Cho pheùp nhöõng khu vöïc (the corresponding indicators will illuminate) vaø kieåm tra khoâng loåi nhöõng baát thöôøng hoaëc coù ñeøn baùo . Neáu baát thöôøng xuaát hieän ngaét nguoàn vaø tìm kieám nguyeân nhaân Neáu moïi thöù bình thöôøng noái heä thoáng vôùi nguoàn chính (220Va.c). Sau vaøi giaây ñeøn baùo “POWER” (nguoàn ñaõ ñöôïc noái ) seõ baät saùng 7. YÙ NGHÓA NHÖÕNG ÑEØN BAÙO VAØ NHÖÕNG KIEÅM SOÙAT. Nhöõng khu vöïc (Ñöôøng1 & 2) Traïng thaùi cuûa 1 trong 2 khu vöïc ñöôïc hieån thò bôûi 4 ñeøn saùng vaø noái / ngaét maïch chòu taùc ñoäng bôûi vieäc söû duïng 2 coâng taéc baám Nhöõng ñeøn hieån thò cho nhöõng tín hieäu treân (Fig. 1) CHO PHEÙP/ KHOÂNG CHO PHEÙP : lieân quan ñeán nhöõng nut baám cuøng teân . Ñeøn saùng khi khu vöïc ñöôïc pheùp (ñang hoïat ñoäng) Ñeøn taét khi khu vöïc khoâng hoïat ñoäng .Traïng thaùi naøy ñöôïc bieåu thò bôûi chuoâng ,cho aâm thanh ngaét quaõng LOÅI MAÏCH MÔÛ: Tín hieäu ñöôøng doø moät loåi maïch môû. Khi moät maïch môû seõ ñöôïc giaùm saùt lieân tuïc maëc duø khu vöïc ñoù khoâng hoïat ñoäng LOÅI ÑOÛAN MAÏCH: hoïat ñoäng gioáng tröôøng hôïp treân nhöng laø loåi ñoûan maïch. CHAÙY: ñeøn baùo saùng leân khi moät hoaëc nhieàu boä phaän doø hoaëc nhöõng nuùt baám lieân quan ñeán nhöõng khu vöïc bò kích hoïat . Moät soá lôùn boä phaän doø ôû traïng thaùi “caûnh baùo” khoâng laøm heä thoáng vaøo tình traïng ñoûan maïch .Loåi naøy duø coù taêng leân cuõng khoâng aûnh höôûng gì ñeán nhöõng thieát bò hieån thò Khi khu vöïc bò ngaét ra (khoâng hoïat ñoäng) caùc thieát bò hieån thò baèng aùnh saùng vaø aâm thanh coù theå kích hoïat ñoäc laäp hoaëc tuøy yù hay khoâng .Tuy nhieân khoâng coù tröôøng hôïp heä thoáng xöû lyù coøi baùo (CN2 and CN3 Fig. 15) Goàm nhöõng thieát bò hieån thò sau (Fig. 1) . Boä phaän heä thoáng ñieàu khieån chung . TIEÀN BAÙO ÑOÄNG: ngay sau khi chaùy phaùt sinh ôû baát cöù khu vöïc naøo .Boä phaän baùo ñoäng sô caáp baét ñaàu ñeám ngöôïc . Thôøi gian naøy coù theå caøi ñaët tuøy theo giaù trò chuùng ta muoán giöûa 0 vaø 4 phuùt .Thôøi gian naøy ñi tröôùc söï kích hoïat cuûa heä thoáng baùo ñoäng chung .Noù keát hôïp chaët cheû vôùi 1 söï kích hoïat chuyeån tieáp trong thôøi gian tieàn baùo ñoäng .Nhö vaäy cho pheùp chuyeån tín hieäu baèng nhöõng thieát bò hieån thò hoaëc baèng moät hieån thò chieáu saùng beân ngoøai . BAÙO ÑOÄNG : nhöõng daáu hieäu cuûa söï kích hoïat heä thoáng baùo ñoäng toång .Söï baùo ñoäng naøy coù theå naøy coù theå cuõng bò kích hoïat hoaëc khoâng kích hoïat bôûi vieäc duøng nuùt “SOUNDES OUTPUT”. LOÅI CUÛA NHÖÕNG BOÄ PHAÄN PHAÙT AÂM THANH: coù loåi treân ñöôøng daây baùo ñoäng chung. LOÅI TOÅNG QUAÙT: ñeøn saùng leân khi coù loåi cuûa ñöôøng daây. NHAÄN BIEÁT: ngaét tín hieäu baèng tay nhöõng aâm thanh taïo bôûi nhieàu nguyeân nhaân khaùc nhau . NGUOÀN ÑIEÄN: toàn taïi nguoàn ñieän chính A/C ñang cung caáp. Taét ñi khi thöû baèng nguoàn pin. PIN : Pin yeáu thì ñeøn saùng leân. Ghi nhôù laïi söï coá dieän theá yeáu ñi khi kieåm tra .Neáu ñieän theá trôû laïi ñuùng thì ñeøn seõ taét. Coøi baùo coù theå hoïat ñoäng trong baát cöù nhöõng tröôøng hôïp sau: Lieân tuïc : ñieän A/C coù vaán ñeà Ngaét quaõng: khu vöïc khoâng ñöôïc noái ñöôøng day Keâu lieân tuïc : coù baùo ñoäng Baùo ñoäng baèng coøi öu tieân cho nhöõng loåi cuûa heä thoáng sau môùi ñeán ñöôøng daây khoâng noái ñeán caùc khu. Nhöõng chöùc naêng cuûa nuùt ñieàu khieån : AÂM THANH PHAÙT RA: cho pheùp kích hoïat baèng tay coøi haëc chuoâng baùo ñoäng khi caàn thieát .Thí duï nhö caàn phaûi sô taùn ra khoûi nhaø cao taàng . Noù cuõng cho pheùp ngaét coøi baùo ñoäng trong giai ñoïan tieàn baùo ñoäng. NHAÄN BIEÁT: ngaên caùc thieát bò aâm thanh beân trong(coøi )moïi bieán coá laø söï kích hoïat töông öùng.Khi xaûy ra 1 bieán coá môùi heä thoáng seõ baùo ñoäng laïi vôùi nhöõng nhòp aâm thanh töông öùng. PHÍM BAÁM CHO PHEÙP: khi truy caäp 1 chöùc naêng nuùt naøy caàn ñöôïc aán ñoàng thôøi vôùi nuùt chöùc naêng töông öùng.Caùch vaän haønh naøy coù theå laïm duïng neáu caàn baèng caùch caøi ñaët 1 caàu noái beân trong khi laép ñaët (Xem caàu noái CN6 hình 15) ÑEØN KIEÅM TRA: Taát caû ñeøn Led töông öùng saùng leân ñoàng thôøi ôû phía tröôùc baûng sau moät bieán coá.Caøi ñaët laïi heä thoáng ñeøn Led sau moät bieán coá ñöïôc kieåm tra hoaëc hieäu chænh Traïng thaùi cuûa moät module choáng chaùy tieâu bieåu bôûi 5 ñeøn Led .Heä thoáng choáng chaùy naøy coù theå ñöôïc noái hoaëc ngaét töï ñoäng baèng cheá ñoä töï ñoängqua vieäc aán nuùt “ENABLE/DISABLE” treân baûng heä thoáng choáng chaùy. 7.3 Quy trình vaän haønh chöõa chaùy (FC220C vaø FC220CLC) LOÅI CUÛA BOÄ PHAÄN PHAÙT AÂM: lieân quan ñeán nhöõng nuùt baám cuøng teân .Ñeøn saùng neáu choáng chaùy töï ñoäng hoïat ñoäng hoaëc ngöôïc laïi . Ñeå thöïc hieän aán ñoàng thôøi nuùt “ENABLE KEY” neáu choïn cheá ñoä naøy ñeå laäp trình. (xem caàu CN6 hình 15) CAÛNH BAÙO SÔÙM (TIEÀN CAÛNH BAÙO): ñeøn saùng trong giai ñoïan caûnh baùo sôùm. MÔÛ RA (Phoùng ra): cho bieát kích hoïat choáng chaùy = van (Khi vieäc naøy ñöôïc kích hoïat caùc nuùt baám baèng tay .Xem phaàn 2..7 the RELEASED, Trigger, LED will go off if the manual inhibition push-button is pressed, provided it is in the rest state). SÖÙC NEÙN THAÁP: chæ cho bieát aùp suaát cuûa chaát choáng chaùy giaõm . LOÅI ÑOAÛN MAÏCH VAØ MAÏCH HÔÛ: cho bieát loåi maïch hôû hoaëc ñoûan maïch (tuaàn töï) treân ñöôøng day phaùt ñoäng choáng chaùy (electro=valve). Caû hai tröôøng hôïp naøy ñeøn ñeàu baät saùng neáu aán nuùt. KIEÅM TRA CUOÁI CUØNG : . Tröôùc khi thöïc hieän kieåm tra nhö ñaõ moâ taû,haõy chuù yù nhöõng ñieåm sau: Moïi taùc ñoäng ñeán trung taâm heä thoáng caàn phaûi aán ñoàng thôøi nuùt ‘’ Enable key “ Moïi söï coá xaûy ra seõ kích hoïat coøi baùo beân trong .Vieäc naøy khoâng cho pheùp söû duïng“ACKNOWLEDGE” nuùt baám treân module toång (ñeøn led töông öùng seõ saùng). Khi moät söï coá khaùc xaõy ra noù seõ kích hoïat laïi. Khi moät söï coá xaõy ra sau khi xoùa ñi(trôû laïi cheá ñoä chôø ) caàn phaûi caøi ñaët laïi heä thoáng .Vieäc naøy ñöôïc thöïc hieän baèng vieäc aán nuùt ñieàu khieån khu vöïc töông öùng hai laàn ( enable/ disable) .Cuõng caàn phaûi aán nuùt “ TEST LEDS” ñeå xoùa ñi caùc tín hieäu phaùt phaùt saùng .Tieáp sau hoïat ñoäng naøy heä thoáng seõ taùt kích hoïat neáu nguyeân nhaân söï coá vaãn toàn taïi hoaëc söï coá môùi phaùt sinh Caøi ñaët laïi heä thoáng sau moãi laàn kieåm tra .Hieån thò cuûa “ACKNOWLEDGE” seõ ngaét . Nhöõng loãi truøng laép . Nhöõng ñeøn led töông öùng vaø coøi baùo bò kích hoïat lieân tuïc Nhöõng ñöôøng doø : Laáy ñaàu doø khoûi oå caém seû taïo ra moät maïch hôû treân ñöôøng doø. Ñeøn led “ O.C FAULT “ cuûa vuøng töông öùng vaø ñeøn led “GEN. FAULT” seõ phaùt saùng Ñöôøng doø bò ñoûan maïch taïi baát cöù ñieãm naøo seõ gaây ra loãi ñoûan maïch .Ñeøn Led S.C FAULT vaø ñeøn led “GEN. FAULT” seõ phaùt saùng Coøi baùo ñoäng toång: Bò hôû hay bò ñoûan maïch taïi baát cöù ñieåm naøo treân ñöôøng ra seõ laøm ñeøn “SOUNDERS FAULT” vaø “GEN. FAULT” phaùt saùng. Neân nhôù raèng caàu noái CN1 neân thaùo ra neáu khoâng duøng ñöôøng daãn ñeán module cuoái cuøng (Xem Fig. 15) trong tröôøng hôïp ñöôøng daây coøi baùo ñoäng toång chæ laø ñeå kieåm tra maïch hôû. Ñöôøng daån choáng chaùy (FC220C vaø FC220CLC). Neáu ñöôøng daån ñeán van ñieän töû bò hôû taïi moät ñieåm baát kyø ñeøn led “O.C FAULT” vaø “GEN. FAULT” treân baûng ñieàu khieån seõ baät saùng Neáu ñöôøng daãn bò ñoûan maïch ñeøn led S.C FAULT vaø “GEN. FAULT” .seõ baät saùng treân baûng ñieàu khieån Neân nhôù Jumper CN1 neân gôû boû neáu khoâng söû duïng ñöôøng daån ñeán Module cuoái ( Fig. 12). Trong tröôøng hôïp ñöôøng daån bò ngaét seõ chæ coøn kieåm tra maïch hôû Nguoàn A/C hoûng . Neáu maát nguoàn ñeøn chæ thò töông öùngseõ taét vaø coøi baùo seõ baùo vôùi aâm thanh lieân tuïc .Coøi baùo coù theå ngaét baèng caùch aán nuùt“ACKNOWLEDGE’’ Khi caùc vuøng bò ngaét Nguyeân nhaân naøy seõ laøm hieån thò “ENABLE/DISABLE” taét vaø kích hoïat coøi baùo phaùt ra aâm thanh ngaét quaûng.Ñieàu naøy cuûng xaõy ra trong tröôøng hôïp heä thoáng ñang ôû cheá ñoä töï ñoäng Vuøng baùo ñoäng . Moät ñaàu phun ñöôïc kích hoïat bôûi ñaàu doø löûa trong töøng vuøng Söï vaän haønh nhöõng ñieåm call-points baèng tay neân duøng moät phuï kieän ñeå kieåm tra maø khoâng caàn phaûi ñaäp vôû kính Khi khôûi phaùt moät ñaàu doø hoaëc call-points seõ laøm thieát bò hieån thò “FIRE” cuûa vuøng töông öùng baät saùng vaø chuoâng baùo phaùt ra aâm thanh ngaét quaûng ôû nhòp ñoä nhanh Vuøng töï ñoäng seõ bò kích hoïat Cuøng luùc ñeøn Led “PRE-ALARM” baät saùng treân baûng ñieàu khieån chöông trình baùo ñoäng sô khôûi seõ baét ñaàu ñeám (nay coù theå laø 0 )vaø baùo ñoäng sô khôûi seõ bò kích hoïat (xem phaàn phuï 5.2) Neáu vuøng naøy khoâng bò ngaét hoaëc nuùt “SOUNDERS OUTPUT” ñöôïc aán tröôùc thôøi gian baùo ñoâng sô khôûi .Ñeøn led “ALARM” seõ saùng treân baûng ñieàu khieån vaø coøi baùo ñoäng toång ñöôïc kích hoïat. Cuøng luùc ñeøn “PRE-ALARM” seõ taét vaø nhöõng tín hieäu lieân heä seõ bò ngaét Sau khi tín hieäu baùo ñoäng toång bò kích hoïat coù theå ngaét tín hieäu baùo ñoäng baèng caùch aán nuùt “SOUNDERS OUTPUT”treân baûng ñieàu khieån CHUÙ YÙ : kieåm tra naøy coù theå thöïc hieän vôùi vuøng khoâng hoïat ñoäng neáu Jumper CN2 ñöôïc thaùo ra (Fig. 15). Ñieàu naøy coù theå cho pheùp kieåm tra hoïat ñoäng cuûa vuøng maø khoâng sôï coøi baùo ñoäng khôûi phaùt Choáng chaùy (FC220C vaø FC220CLC). CHUÙ YÙ : haõy chaéc chaén van ñieän töû ñaõ ñöôïc ngaét tröôùc khi thöïc hieän kieåm tra naøy. Caøi ñaët laïi thôøi gian cho FC220C (Ñaàu doø coù doøng giôùi haïn). Vuøng 1 duøng cho choáng chaùy. Khi ñaàu doø thöù nhaát ñöôïc kích hoïat thôøi gian caøi ñaët baét ñaàu ñeám ngöôïc neáu khoâng coù ñaàu doø thöù hai ñi vaøo traïng thaùi ø baùo ñoäng (Fig 15 ) .Ñöôøng daây daån cuûa nhöõng ñaàu doø lieân quan ñeán vuøng 1 seõ töï ñoäng caøi ñaët laïi thôøi gian gian khoûang 4giaây . Baùo ñoäng chính seõ bieán maát neáu caùc ñaàu doø khoâng khôûi phaùt laïi Neáu moät ñaàu doø thöù hai ñi vaøo traïng thaùi baùo ñoäng tröôùc giai ñoïan naøy thì moät trong hai ñieàu coù theå xaûy ra : Thôøi gian tieàn khôûi phaùt coù theå baét ñaàu (kieåm tra keùp). ñeøn PREWARNING baät saùng Baét ñaàu “ reset time “ laàn 2 (kieåm tra 3laàn )trong tröôøng hôïp sau noù seõ laäp laïi nhö ñaõ moâ taû ôû treân . Nhö theá ñaàu doø thöù 3 neân ñuôïc khôûi phaùt tröôùcôû phaàn cuoái cuûa thôøi gian ñöôïc caøi ñaët laïi .Thôøi gian tieàn khôûi phaùt seõ baét ñaàu vaø tín hieäu töông öùng seõ ñöôïc kích hoïat ( Xem phaàn phuï 2.8.2) Caøi ñaët laïi thôøi gian cho FC220CLC (ñaàu doø khoâng giôùi haïn doøng). 2 vuøng caàn cho choáng chaùy . Neáu vieäc baùo ñoäng gaây ra bôûi moät trong 2 vuøng thôøi gian caøi ñaët seõ baét ñaàu hoïat ñoäng.Neáu khoâng coù baùo ñoäng ôû nhöûng vuøng khaùc ôû cuoái thôøi kyø ,baõng ñieàu khieån seõ töï ñoäng reset hai ñöôøng doø lieân quan ñeán 2 vuøng vôùi thôøi gian khoûang 4 giaây. Ñieàu naøy coù theå laøm baùo baùo ñoäng chính bieán maát neáu ñaàu doø khoâng ñöôïc kích hoïat laïi . Noùi caùch khaùc noù seõ baét ñaàu ñeám thôøi gian caøi ñaët moät laàn nöûa vaø nhö vaäy tieán trình ñöôïc laäp laïi Neáu sau khi moät vuøng ñaõ ñi vaøo traïng thaùi baùo ñoäng ,moät baùo ñoäng xuaát hieän trong moät vuøng khaùc tröùôc khi keát thuùc thôøi gian caøi ñaët , thì coù theå thôøi gian tieàn khôûi phaùt seõ baét ñaàu vaø tín hieäu phaùt töông öùng seõ ñöôïc kích hoïat (phaàn phuï 2.8.2) Naïp vaøo baèng tay vaø choáng chaùy vôùi FC220C vaø FC220CLC. Neáu “thôøi gian tieàn khôûi phaùt” ( ñeøn PREWARNING saùng leân ) keát thuùc maø khoâng coù taùc ñoäng cuûa ngöôøi söû duïng ,van ñieän töû cuûa heä thoáng choáng chaùy seõ khôûi phaùt (khoâng coù xaõ ga trong tröôøng hôïp naøy )vaø ñeøn led “RELEASED” (Trigger) seõ saùng leân Vieäc khôûi phaùt coù theå boû qua trong giai ñoïan naøy baèng vieäc aán nuùt Stop treân Remote (khoâng cho pheùp söû duïng baèng tay) hoaëc söû duïng nuùt “ENABLE/DISABLE” treân baûng ñieàu khieån Heä thoáng choáng chaùy cuõng coù theå cho pheùp khôûi phaùt baèng tay baát cöù luùc naøo thoâng qua söû duïng nuùt baám “Manual trigger” treân remote (xem phaàn phuï 2.8.1 vaø 7.3) |
| --- | --- |